## Archive
Week | WO_Date | NOTIFICATION# | PLANT | DEPARTMENT | WO TYPE | WO_NO | DISCIPLINE | Description | Function Location | Maintenance_Object_Description | Planned_Start_Date | Actual_Start_Date | Planned Finish Date | Actual_Finish_Date | Status | Extended_Status | Estimated Manpower | Actual Manpower | Estimated Duration (hrs) | Actual Duration (hrs) | Estimated Total ManHours | Actual Total ManHours | PTW NO | MSRF | ASSIGNED SUPERVISOR | FEEDBACK | SPV NAME | SPV UPDATE DATE | CONFORM BY ( FOR OPRATION ) | CONFORM DATE | OPERATION RESULT | OPERATION NOTE | ATTACHMENTS | CM TOMORROW | UPDATE HISTORY
W26-26 | 2026-06-24 | 110000400192 | PPG | 19MSTAT | CM | 210000345195 | 19MSTAT | CARRY OUT CM TO REPLACE HOSE FOR DEHUMIDIFIER OF AIR DRYER GT12 | Z019-4702-12MBL93 | AIR DRYER FOR GT AIR INTAKE SYSTEM |  |  |  | 2026-06-30 | COMPLETED |  |  | 1 |  | 1 |  | 1 |  |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | The hose cleaned and patch repaired . | CHIKH SOUHEIB | 2026-06-30 | AHMED ABDULLAH | 2026-07-02 | Complete |  | PDF Gallery_20260630_113310.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/87cd3eb0-8e8f-4d43-ad67-78154e7dfb64/supervisor/210000345195_19MSTAT_20260630083501.pdf |  | 7/2/2026, 11:07:27 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/30/2026, 11:36:53 AM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED The hose cleaned and patch repaired . 6/30/2026, 11:35:03 AM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345195.pdf Created from notification 110000400192 by ABDELNASSER at 2026-06-24T06:17:37.906Z
W27-26 | 2026-07-02 | 110000400721 | PPG | 19HVAC | CM | 210000345518 | 19HVAC | CARRY OUT CM TO CHECK AND FIX THE HVAC UNIT HAS ONE CONDENSER FAN BROKEN | Z019-4701-11SAD30AH040 | ELECTRIC MODULE HVAC UNIT |  |  |  | 2026-07-03 | COMPLETED |  |  | 2 |  | 3 |  | 6 | 1999 |  | AHMED MAGID; AHMED SAMIR; FARAG | Work is done and completed as attached per work order. | AHMED SAMIR | 2026-07-03 | WAQAS SAJID | 2026-07-03 | Complete |  | 210000345518.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/31392fe2-89ed-4cf1-84b5-8419fc2f4fcb/supervisor/210000345518_19HVAC_20260703081751.pdf | {"active":true,"addedAt":"2026-07-02T11:10:45.743Z","addedBy":"AHMED SAMIR","addedByUsername":"ahmed samir","woNo":"210000345518"} | 7/3/2026, 3:26:29 PM - Bulk operation confirmation By: WAQAS SAJID COMPLETED / Complete 7/3/2026, 11:20:51 AM - Supervisor update By: AHMED SAMIR COMPLETED PTW: 1999 Work is done and completed as attached per work order. 7/3/2026, 11:17:58 AM - Attachment uploaded By: AHMED SAMIR ONGOING 19HVAC - 210000345518.pdf 7/2/2026, 2:10:45 PM - CM's for tomorrow By: AHMED SAMIR ONGOING Added to CM's for tomorrow by AHMED SAMIR. 7/2/2026, 8:40:41 AM - Work order details edit By: MOHAMMED HASSAN ONGOING Details edited by MOHAMMED HASSAN Created from notification 110000400721 by MOHAMMED HASSAN at 2026-07-02T04:27:33.505Z
W24-26 | 2026-06-10 | 110000398749 | PPG | 19MSTAT | CM | 210000344483 | 19MSTAT | CARRY OUT CM TO CHECK AND FIX TANK 2 OF ULTRA FILTRATION SYS DUE TO LEAKAGE FROM THE BASE | Z019-5220-90GCK14BB002 | UF PERMEATE TANK 2 |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1941 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | Tank was isolated, drained, cleaned and visually inspected. No structural deformation or obvious defects were identified. A specialized inspection is required. | CHIKH SOUHEIB | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | PDF Gallery_20260701_173012.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/9c807302-25d9-40b5-82e0-0f1af5566ad0/supervisor/210000344483_19MSTAT_20260701143100.pdf | {"active":true,"addedAt":"2026-06-19T10:47:06.335Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000344483"} | 7/2/2026, 11:07:27 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 5:33:10 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1941 Tank was isolated, drained, cleaned and visually inspected. No structural deformation or obvious defects were identified. A specialized inspection is required. 7/1/2026, 5:31:02 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:30:26 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:29:27 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:29:07 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:28:47 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:14:01 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 7/1/2026, 5:13:08 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 6/20/2026, 3:30:37 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344483.pdf 6/20/2026, 1:52:42 PM - Attachment uploaded By: IMAN ONGOING 19MSTAT - 210000344483.pdf 6/19/2026, 1:47:06 PM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB.
W27-26 | 2026-06-28 | 220001753636 | PPG | 19HVAC | CM | 210000345351 | 19HVAC | CARRY OUT CM TO REPLACE THE COMPRESSOR FOR WTP CONT. 90GCF21GH001 SPLIT TYPE AC GRA | Z019-5220-90GCF21GH001SP01 | WTP CONT. 90GCF21GH001 SPLIT TYPE AC GRA |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 4 |  | 8 | 1966 |  | AHMED MAGID; AHMED SAMIR; FARAG | Work is done and completed as attached per work order | AHMED SAMIR | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | 19HVAC_210000345351.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/2b3a525d-ee8e-4ccd-9232-b3b5395ff586/supervisor/210000345351_19HVAC_20260701141521.pdf | {"active":true,"addedAt":"2026-06-29T10:52:44.306Z","addedBy":"AHMED SAMIR","addedByUsername":"ahmed samir","woNo":"210000345351"} | 7/2/2026, 10:57:37 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 5:17:11 PM - Supervisor update By: AHMED SAMIR COMPLETED PTW: 1966 Work is done and completed as attached per work order 7/1/2026, 5:15:28 PM - Attachment uploaded By: AHMED SAMIR ONGOING 19HVAC - 210000345351.pdf 6/29/2026, 1:52:44 PM - CM's for tomorrow By: AHMED SAMIR ONGOING Added to CM's for tomorrow by AHMED SAMIR. Created from notification 220001753636 by MOHAMMED HASSAN at 2026-06-28T06:08:19.444Z
W27-26 | 2026-07-01 | 110000400655 | PPG | 19MSTAT | CM | 210000345505 | 19MSTAT | CARRY OUT CM TO REPLACE POWER OIL FILTER DUE TO HIGH DELTA-P FOR GT14 | Z019-4704-14MBX21AT002 | FILT-2 FOR POWER OIL IN FG CONT SKID |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1969 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | FILTER REPLACED. | CHIKH SOUHEIB | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | PDF Gallery_20260701_174828.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/13f42028-18f1-46fd-97a0-256c029fac2a/supervisor/210000345505_19MSTAT_20260701144957.pdf |  | 7/2/2026, 11:07:27 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 5:53:44 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1969 FILTER REPLACED. 7/1/2026, 5:49:59 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345505.pdf Created from notification 110000400655 by ABDELNASSER at 2026-07-01T10:12:25.128Z
W27-26 | 2026-07-01 | 110000400654 | PPG | 19MSTAT | CM | 210000345504 | 19MSTAT | CARRY OUT CM TO REPLACE LUBE OIL FILTER DUE TO HIGH DELTA-P FOR GT13 | Z019-4703-13MBV21AT001 | FILT LO CENTRIFUGAL PUMP1 SUCT OF LO MOD |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1968 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | FILTERS REPLACED | CHIKH SOUHEIB | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | PDF Gallery_20260701_174809.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/6ad948e4-5311-498a-8c11-1eb75740c8b9/supervisor/210000345504_19MSTAT_20260701145429.pdf |  | 7/2/2026, 11:07:27 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 5:55:49 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1968 FILTERS REPLACED 7/1/2026, 5:54:31 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345504.pdf Created from notification 110000400654 by ABDELNASSER at 2026-07-01T10:11:18.727Z
W27-26 | 2026-07-01 | 110000400653 | PPG | 19MSTAT | CM | 210000345503 | 19MSTAT | CARRY OUT CM TO REPLACE POWER OIL FILTER DUE TO HIGH DELTA-P FOR GT11 | Z019-4701-11MBX21AT001 | FILT-1 FOR POWER OIL IN FG CONT SKID |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1967 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | FILTER REPLACED | CHIKH SOUHEIB | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | PDF Gallery_20260701_174750.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/ada3370c-0406-4e53-9ed1-afa2348d6481/supervisor/210000345503_19MSTAT_20260701145653.pdf |  | 7/2/2026, 11:07:27 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 5:57:38 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1967 FILTER REPLACED 7/1/2026, 5:56:55 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345503.pdf Created from notification 110000400653 by ABDELNASSER at 2026-07-01T10:10:01.271Z
W26-26 | 2026-06-25 | 110000400170 | PPG | 19ELEC | CM | 210000345262 | 19ELEC | CARRY OUT CM TO CHECK AND FIX EARTH FAULT ALARM | Z019-9000-90BTL10 | BATT CHARGER FOR BALANCE OF PLANT DC UPS |  |  |  | 2026-07-01 | COMPLETED |  |  | 2 |  | 1 |  | 2 |  |  | BILEL DJEKRIF; MANISHKUMAR RATILAL PATEL; SAMER SAMIR; VITALIY GORSHKOV | Alarm have been cleared | BILEL DJEKRIF | 2026-07-01 | AHMED ABDULLAH | 2026-07-02 | Complete |  | WO.210000345262 Carry out CM to check and fix earth fault alarm..pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/ab014d74-a2f1-44d0-83a9-8de2a788a8ee/supervisor/210000345262_19ELEC_20260701075218.pdf |  | 7/2/2026, 10:56:48 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/1/2026, 10:55:46 AM - Supervisor update By: BILEL DJEKRIF COMPLETED Alarm have been cleared 7/1/2026, 10:52:29 AM - Attachment uploaded By: BILEL DJEKRIF ONGOING 19ELEC - 210000345262.pdf 6/30/2026, 5:47:59 PM - Attachment deleted By: BILEL DJEKRIF ONGOING 19ELEC - 210000345262.pdf 6/30/2026, 5:39:42 PM - Attachment uploaded By: BILEL DJEKRIF ONGOING 19ELEC - 210000345262.pdf Created from notification 110000400170 by ABDELNASSER at 2026-06-25T09:12:27.523Z
W27-26 | 2026-07-01 | 110000400649 | PPG | 19MROT | CM | 210000345484 | 19MROT | CARRY OUT CM TO CHECK AND REPLACE BELT FOR STP AIR BLOWER-3 | Z019-5700-90GQA05AN003 | AIR BLOWER 3 |  |  |  | 2026-06-30 | COMPLETED |  |  | 3 |  | 2 |  | 6 | 1975 |  | ADHEM ELSAYED HANAFY; AMR MOHAMED; MOHAMED AHMED; MAHMOUD OMARA | Open work permit with Elec isolation certificate check item subject to maintenance for HSE conditions check perfect condition of all guards and warning symbols check tightness of all nuts and bolts. checked old belts found in bad condition so replaced by new belts. checked oil level and refilled to adjust level. Checked and cleaned air filter. check perfect condition of all accessories installed clean area and equipment after the work inform control room of ending of the works close the work permit | MAHMOUD OMARA | 2026-07-02 | AHMED ABDULLAH | 2026-07-02 | Complete |  | STP Blower 3 (01-07-2026).pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/058fcd0d-fd28-4a3a-b141-ffee6a09b3fb/supervisor/210000345484_19MROT_20260702060711.pdf |  | 7/2/2026, 10:58:45 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/2/2026, 9:11:24 AM - Supervisor update By: MAHMOUD OMARA COMPLETED PTW: 1975 Open work permit with Elec isolation certificate check item subject to maintenance for HSE conditions check perfect condition of all guards and warning symbols check tightness of all nuts and bolts. checked old belts found in bad condition so replaced by new belts. checked oil level and refilled to adjust level. Checked and cleaned air filter. check perfect condition of all accessories installed clean area and equipment after the work inform control room of ending of the works close the work permit 7/2/2026, 9:07:14 AM - Attachment uploaded By: MAHMOUD OMARA ONGOING 19MROT - 210000345484.pdf Created from notification 110000400649 by ABDELNASSER at 2026-07-01T05:57:43.768Z
W26-26 | 2026-06-25 | 110000400380 | PPG | 19DCS | CM | 210000345264 | 19DCS | CARRY OUT CM TO CHECK AND FIX DEW POINT HEAT EXCHANGER 90EKT20CT001, ALL INSTRUMENTATION SIGNALS ARE LOST | Z019-4200-90EKT20CT001 | TEMP TRANS WO/L DEW POINT HEXNGR 2 |  |  |  | 2026-06-30 | COMPLETED |  |  | 1 |  | 3 |  | 3 |  |  | ABDELRAZEK SAID MOHAMED; MESSAOUD BENMOUIZA; MOHAMED BOUCHACHIA | Under observation | MOHAMED BOUCHACHIA | 2026-07-02 | AHMED ABDULLAH | 2026-07-02 | Complete |  | Feedback WO#210000345264.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/f47d069f-d968-4fb9-aeb8-6f151545faf5/supervisor/210000345264_19DCS_20260702065707.pdf |  | 7/2/2026, 10:53:26 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 7/2/2026, 9:57:31 AM - Supervisor update By: MOHAMED BOUCHACHIA COMPLETED Under observation 7/2/2026, 9:57:10 AM - Attachment uploaded By: MOHAMED BOUCHACHIA ON HOLD / WAITING OPERATION 19DCS - 210000345264.pdf 6/30/2026, 7:51:05 AM - Bulk supervisor update By: MOHAMED BOUCHACHIA ON HOLD / WAITING OPERATION Under observation 6/29/2026, 9:24:14 AM - Bulk supervisor update By: MOHAMED BOUCHACHIA ONGOING Once the 3-way valve feedback was isolated, all signals were restored. Created from notification 110000400380 by ABDELNASSER at 2026-06-25T09:16:29.215Z
W26-26 | 2026-06-23 | 110000399851 | PPG | 19ELEC | CM | 210000345124 | 19ELEC | CARRY OUT CM TO CHECK AND FIX PULSE AIR COMPRESSOR 2 OF GT14 DUE TO ABNORMAL SOUND | Z019-4704-14MBL54AN002 | AIR COMPRESSOR-2 FOR COMPRESSOR AIR STN |  |  |  | 2026-06-30 | COMPLETED |  |  | 2 |  | 1 |  | 2 |  |  | BILEL DJEKRIF; MANISHKUMAR RATILAL PATEL; SAMER SAMIR; VITALIY GORSHKOV | Inspection done with mechanical team. The current was also monitored and measured.46.3A balanced (Normal operating range). | BILEL DJEKRIF | 2026-06-30 | AHMED ABDULLAH | 2026-07-02 | Complete |  | WO.210000345124 FEEDBACK CARRY OUT CM TO CHECK AND FIX PULS EAI RCOMPRESSOR2 OF GT14 DUE TO ABNORMAL SOUND..pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/4fa081f5-38a1-4723-be2b-bbc0be3d2a19/supervisor/210000345124_19ELEC_20260630144813.pdf |  | 7/2/2026, 10:56:48 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/30/2026, 5:49:15 PM - Supervisor update By: BILEL DJEKRIF COMPLETED Inspection done with mechanical team. The current was also monitored and measured.46.3A balanced (Normal operating range). 6/30/2026, 5:48:18 PM - Attachment uploaded By: BILEL DJEKRIF ONGOING 19ELEC - 210000345124.pdf Created from notification 110000399851 by ABDELNASSER at 2026-06-23T05:24:09.290Z
W25-26 | 2026-06-10 | 110000398580 | PPG | 19INSTR | CM | 210000344458 | 19INSTR | CARRY OUT CM TO CHECK AND FIX FUEL OIL TANK NO.2 LEVEL READS ZERO W HILE TANK IS 1.66M ( CALIBRATION & CHECK REQUIRED ) | Z019-4300-90EGB03CL006 | LEVEL TRANSMITTER FOR FUEL OIL TANK 2 |  |  |  | 2026-06-23 | COMPLETED |  |  | 2 |  | 15 |  | 30 | 1922 |  | HAITHAM MOHAMED; INST-SPV; MOHAMMED HAMED; MOHAMED TOUNI; SAHAYARAJ | Checked parameter value for the transmitter and mapped the tank measuring path. • Adjusted parameter as per mapping result. • TVT-HOVER LEVEL 25% from 40% • ECHO THRESHOLD 2 from 7. • Filling rate: MEDIUM from SLOW. • The actual tank level is now being read by the level transmitter. | SAHAYARAJ | 2026-06-29 | AHMED ABDULLAH | 2026-06-30 | Complete |  | 210000344458.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/412235a6-96cc-4787-956e-d3e59ec7284b/supervisor/210000344458_19INSTR_20260629142856.pdf CALIBRATION CERTIFICATE CL006 26-06-26.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/412235a6-96cc-4787-956e-d3e59ec7284b/supervisor/210000344458_19INSTR_20260630042632.pdf | {"active":false,"addedAt":"2026-06-17T04:26:02.297Z","addedBy":"Sahayaraj","addedByUsername":"sahayaraj","woNo":"210000344458","removedAt":"2026-06-22T09:53:07.887Z","removedBy":"SAHAYARAJ","removedByUsername":"sahayaraj"} | 6/30/2026, 8:17:42 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/30/2026, 7:26:54 AM - Attachment uploaded By: SAHAYARAJ COMPLETED 19INSTR - 210000344458 (2).pdf 6/30/2026, 7:00:25 AM - Attachment deleted By: SYSTEM ADMIN COMPLETED 19INSTR - 210000344458.pdf 6/29/2026, 5:30:49 PM - Supervisor update By: SAHAYARAJ COMPLETED PTW: 1922 Checked parameter value for the transmitter and mapped the tank measuring path. • Adjusted parameter as per mapping result. • TVT-HOVER LEVEL 25% from 40% • ECHO THRESHOLD 2 from 7. • Filling rate: MEDIUM from SLOW. • The actual tank level is now being read by the level transmitter. 6/29/2026, 5:28:59 PM - Attachment uploaded By: SAHAYARAJ ON HOLD / WAITING OPERATION 19INSTR - 210000344458 (2).pdf 6/23/2026, 2:41:51 PM - Supervisor update By: SAHAYARAJ ON HOLD / WAITING OPERATION Waiting for filling diesel to the tank. Level transmitter under observation. 6/20/2026, 1:56:39 PM - Attachment uploaded By: IMAN ONGOING 19INSTR - 210000344458.pdf 6/17/2026, 7:26:02 AM - CM's for tomorrow By: SAHAYARAJ ONGOING Added to CM's for tomorrow by Sahayaraj.
W26-26 | 2026-06-23 | 110000399850 | PPG | 19MROT | CM | 210000345122 | 19MROT | CARRY OUT CM TO REPLACE BELT FOR AIR BLOWER-1 | Z019-5700-90GQA05AN001 | AIR BLOWER 1 |  |  |  | 2026-06-25 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | ADHEM ELSAYED HANAFY; AMR MOHAMED; MOHAMED AHMED; MAHMOUD OMARA | PTW Opened , replace the old belts with new one keep the Blower out of service due to cooling fan motor damage the new fan requested as new another work order close the ptw | ADHEM ELSAYED HANAFY | 2026-06-25 | AHMED ABDULLAH | 2026-06-29 | Complete |  | AIR BLOWER STP NO 1 SIGNED.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/c31e3ab9-52ee-41df-ae9e-8287fe034302/supervisor/210000345122_19MROT_20260625130923.pdf |  | 6/29/2026, 10:15:27 AM - Operation confirmed By: AHMED ABDULLAH COMPLETED / Complete 6/25/2026, 4:10:40 PM - Supervisor update By: ADHEM ELSAYED HANAFY COMPLETED PTW Opened , replace the old belts with new one keep the Blower out of service due to cooling fan motor damage the new fan requested as new another work order close the ptw 6/25/2026, 4:09:25 PM - Attachment uploaded By: ADHEM ELSAYED HANAFY ONGOING 19MROT - 210000345122.pdf Created from notification 110000399850 by ABDELNASSER at 2026-06-23T05:02:07.068Z
W26-26 | 2026-06-25 | 110000400346 | PPG | 19GTG | CM | 210000345236 | 19GTG | OPEN FINDINGS AND OUTSTANDING ACTIVITIES Pulse Filters (some filters with gabs on base)" to Correct installation and torque as spec. "Online Washing System (Trace oil and dust observed)"need Clean by dry rags. "Offline Washing System (Trace oil and dust observed)" need Clean by dry rags. "Compressor Intake Housing (Water drainpipe blocked)" need Clean and inspect. "VIGV (Minor deposit on platform)" need Clean with soft rags and monitor. "VIGV System (Minor oil leakage in front seal)" need Clean and monitor "Rotor & Bearing: Bearing 1 (Dirt such insulation and lube oil pan with drainpipe disconnect.) need Clean and re connect drainpipe. "Rotor & Bearing: Bearing 2 (Minor oil mist and dust accumulation seen) need Clean | Z019-4702-12MBA30 | GAS TURBINE-2; FOR Z019-4702 |  |  |  | 2026-06-29 | COMPLETED |  |  | 3 |  | 5 |  | 15 | 1930 |  | AHMED EMARA; ALI ELSAYED | The work has been completed. During the inspection, we found that 17 air inlet pulse filters required additional ties, and the issue has been rectified. | AHMED EMARA | 2026-06-29 | AHMED ABDULLAH | 2026-06-29 | Complete |  | WO 210000345236.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/7624df57-c77c-4611-bcb8-ce8097a5177f/supervisor/210000345236_19GTG_20260629045003.pdf |  | 6/29/2026, 10:09:32 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/29/2026, 7:58:32 AM - Supervisor update By: AHMED EMARA COMPLETED PTW: 1930 The work has been completed. During the inspection, we found that 17 air inlet pulse filters required additional ties, and the issue has been rectified. 6/29/2026, 7:50:05 AM - Attachment uploaded By: AHMED EMARA ONGOING 19GTG - 210000345236.pdf Created from notification 110000400346 by ABDELNASSER at 2026-06-25T12:31:56.683Z
W26-26 | 2026-06-23 | 110000400036 | PPG | 19MROT | CM | 210000345123 | 19MROT | CARRY OUT CM TO CHECK AND FIX ALIGNMENT FOR BWRO PUMP NO.3 | Z019-5220-90GCK35AP003 | BWRO PERMEATE TRANSFER PUMP 3 |  |  |  | 2026-06-25 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1855 |  | ADHEM ELSAYED HANAFY; AMR MOHAMED; MOHAMED AHMED; MAHMOUD OMARA | Open ptw, electric isolation , informed ccr with starting of the job , dismantle the coupling guard and check alignment , found ok "within range" decoupling the motor and check the vibration for solo test rung for motor found ok install the coupling between the motor and the pump and lift the isolation and put the skid in-service under observation close the PTW | ADHEM ELSAYED HANAFY | 2026-06-25 | AHMED ABDULLAH | 2026-06-29 | Complete |  | BWRO PUMP 111.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/0a18cba9-6615-419f-bcca-80b20254def1/supervisor/210000345123_19MROT_20260625130805.pdf |  | 6/29/2026, 10:15:36 AM - Operation confirmed By: AHMED ABDULLAH COMPLETED / Complete 6/25/2026, 4:08:56 PM - Supervisor update By: ADHEM ELSAYED HANAFY COMPLETED PTW: 1855 Open ptw, electric isolation , informed ccr with starting of the job , dismantle the coupling guard and check alignment , found ok "within range" decoupling the motor and check the vibration for solo test rung for motor found ok install the coupling between the motor and the pump and lift the isolation and put the skid in-service under observation close the PTW 6/25/2026, 4:08:06 PM - Attachment uploaded By: ADHEM ELSAYED HANAFY ONGOING 19MROT - 210000345123.pdf 6/23/2026, 8:55:32 AM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER Created from notification 110000400036 by ABDELNASSER at 2026-06-23T05:22:05.845Z
W25-26 | 2026-06-19 | 110000399659 | PPG | 19MSTAT | CM | 210000344975 | 19MSTAT | CARRY OUT CM TO REPLACE POWER OIL FILTER | Z019-4702-12MBX21AT041 | FILT-1 FOR POWER OIL IN FUEL OIL MODULE |  |  |  | 2026-06-21 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1857 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | FILTER REPLACED | CHIKH SOUHEIB | 2026-06-21 | AHMED ABDULLAH | 2026-06-29 | Complete |  | PDF Gallery_20260621_172748.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/1f3cd475-2c79-4905-b2e0-b420373bbaa8/supervisor/210000344975_19MSTAT_20260621143230.pdf | {"active":true,"addedAt":"2026-06-20T12:33:20.658Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000344975"} | 6/29/2026, 10:03:10 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/21/2026, 5:33:57 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1857 FILTER REPLACED 6/21/2026, 5:32:32 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344975.pdf 6/20/2026, 4:30:15 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344975.pdf 6/20/2026, 3:33:20 PM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/19/2026, 6:22:16 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 6:12:48 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:41:28 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344975.pdf Created from notification 110000399659 by HUSSAIN OTHMAN at 2026-06-19T11:38:11.520Z
W26-26 | 2026-06-22 | 110000399853 | PPG | 19MSTAT | CM | 210000345093 | 19MSTAT | CLOGGED SUMP FOR THE DRAIN OF EYE WASH IN STP AREA | Z019-7000-EYEWASH-07 | STP AREA - EYE WASH WITH SHOWER |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 2.5 |  | 5 | 1911 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED | CHIKH SOUHEIB | 2026-06-26 | AHMED ABDULLAH | 2026-06-29 | Complete |  | 07.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/bec6b6b1-b2e5-4c34-9db9-e10c1f103db7/supervisor/210000345093_19MSTAT_20260626114543.pdf | {"active":true,"addedAt":"2026-06-23T07:19:13.869Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000345093"} | 6/29/2026, 10:16:03 AM - Operation confirmed By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 2:52:30 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1911 INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED 6/26/2026, 2:45:45 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345093.pdf 6/26/2026, 2:45:32 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345093.pdf 6/23/2026, 10:19:13 AM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/22/2026, 9:03:33 AM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000345093.pdf Created from notification 110000399853 by HUSSAIN OTHMAN at 2026-06-22T06:00:00.563Z
W26-26 | 2026-06-22 | 110000399854 | PPG | 19MSTAT | CM | 210000345094 | 19MSTAT | CLOGED EYE WASH IN FIRE BRIGADE BUILDING | Z019-7000-EYEWASH-08 | FIGHER FIGHTING - EYE WASH WITH SHOWER |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 2.5 |  | 5 | 1911 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED | CHIKH SOUHEIB | 2026-06-26 | AHMED ABDULLAH | 2026-06-29 | Complete |  | 08.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/f91b0b21-8c23-4495-9956-6f7b3f74ff2a/supervisor/210000345094_19MSTAT_20260626114557.pdf | {"active":true,"addedAt":"2026-06-23T07:18:49.729Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000345094"} | 6/29/2026, 10:15:53 AM - Operation confirmed By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 2:52:30 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1911 INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED 6/26/2026, 2:45:58 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345094.pdf 6/26/2026, 2:45:12 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000345094.pdf 6/23/2026, 10:18:49 AM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/22/2026, 9:03:58 AM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000345094.pdf Created from notification 110000399854 by HUSSAIN OTHMAN at 2026-06-22T06:00:14.295Z
W25-26 | 2026-06-18 | 110000399700 | PPG | 19INSTR | CM | 210000344920 | 19INSTR | CARRY OUT CM TO CHECK AND FIX THE SLUG CATCHER LEVEL TRANSMITTER | Z019-4200-90EKR01CL001 | LEVEL ITRANS SLUG CATCHER 90EKR01BB001 |  |  |  | 2026-06-21 | COMPLETED |  |  | 2 |  | 7 |  | 14 | 1864 |  | HAITHAM MOHAMED; INST-SPV; MOHAMMED HAMED; MOHAMED TOUNI; SAHAYARAJ | LT float chamber drained, flushed and cleaned. Simulation checked. found missing one support clamp for the LT sensor and fixed. Now transmitter working normal. | SAHAYARAJ | 2026-06-29 | AHMED ABDULLAH | 2026-06-29 | Complete |  | INSTR - 210000344920 LT-001.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/f8b8d719-5609-4014-8d8a-544cc7ef78ff/supervisor/210000344920_19INSTR_20260629053524.pdf | {"active":false,"addedAt":"2026-06-20T07:41:25.413Z","addedBy":"SAHAYARAJ","addedByUsername":"sahayaraj","woNo":"210000344920","removedAt":"2026-06-21T10:16:53.077Z","removedBy":"SAHAYARAJ","removedByUsername":"sahayaraj"} | 6/29/2026, 10:04:44 AM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/29/2026, 8:42:22 AM - Supervisor update By: SAHAYARAJ COMPLETED PTW: 1864 LT float chamber drained, flushed and cleaned. Simulation checked. found missing one support clamp for the LT sensor and fixed. Now transmitter working normal. 6/29/2026, 8:35:26 AM - Attachment uploaded By: SAHAYARAJ ON HOLD / WARRANTY ISSUE 19INSTR - 210000344920.pdf 6/23/2026, 3:24:24 PM - Supervisor update By: SAHAYARAJ ON HOLD / WARRANTY ISSUE Three days remain for under observation. 6/21/2026, 1:20:52 PM - Attachment deleted By: SYSTEM ADMIN ONGOING 19INSTR - 210000344920.pdf 6/20/2026, 11:04:03 AM - Attachment uploaded By: IMAN ONGOING 19INSTR - 210000344920.pdf 6/20/2026, 10:41:25 AM - CM's for tomorrow By: SAHAYARAJ ONGOING Added to CM's for tomorrow by SAHAYARAJ. Created from notification 110000399700 by IMAN at 2026-06-18T04:55:26.365Z
W26-26 | 2026-06-25 | 110000400417 | PPG HV SS | 19HVPT SS | CM | 210000345265 | 19HVPT SS | CARRY OUT CM TO CHECK & FIX METERING LAPNG LAPTOP HAS ALOUD VOICE | Z999-9700-90AQA30GK002 | METERING PANEL-2 FOR PPG SUB-STATION |  |  |  | 2026-06-27 | COMPLETED |  |  | 2 |  | 4 |  | 8 | 1927 |  | AHMED HUSSIEN; AMER JAMAL; AMR GAMAL; HASHIM ISMAIL; ISLAM FATHI; KAREEM ABDELMAWLA; KARIM DALY; MOHAMMED KHALIF; RAMADAN GAMAL; SAAD AWNY | The internal processor cooling fan has been repaired, it is now in good condition, and it will be kept under observation. | AHMED HUSSIEN | 2026-06-28 | BAZYA DMIITRIY | 2026-06-28 | Complete |  | Metering laptop .pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/d946f162-b442-4f83-8a4a-4202767b3d88/supervisor/210000345265_19HVPT_SS_20260628081201.pdf | {"active":true,"addedAt":"2026-06-26T12:49:37.828Z","addedBy":"BAZYA DMIITRIY","addedByUsername":"bazya dmiitriy","woNo":"210000345265"} | 6/28/2026, 6:07:58 PM - Bulk operation confirmation By: BAZYA DMIITRIY COMPLETED / Complete 6/28/2026, 11:14:05 AM - Supervisor update By: AHMED HUSSIEN COMPLETED PTW: 1927 The internal processor cooling fan has been repaired, it is now in good condition, and it will be kept under observation. 6/28/2026, 11:12:03 AM - Attachment uploaded By: AHMED HUSSIEN ONGOING 19HVPT SS - 210000345265.pdf 6/26/2026, 3:49:37 PM - CM's for tomorrow By: BAZYA DMIITRIY ONGOING Added to CM's for tomorrow by BAZYA DMIITRIY. Created from notification 110000400417 by ABDELNASSER at 2026-06-25T09:30:57.650Z
W26-26 | 2026-06-24 | 110000400173 | NEW ZUBAIR MV SS | 19HVPT SS | CM | 210000345187 | 19HVPT SS | Install Undervoltage Relay of LV Panel New Zubair | Z913-9200-EL-102 | LIGHTING & SMALL POWER DB (LSPDB) |  |  |  | 2026-06-24 | COMPLETED |  |  | 3 |  | 1.5 |  | 4.5 | 1903 |  | AHMED HUSSIEN; AMER JAMAL; AMR GAMAL; HASHIM ISMAIL; ISLAM FATHI; KAREEM ABDELMAWLA; KARIM DALY; MOHAMMED KHALIF; RAMADAN GAMAL; SAAD AWNY | -Obtained permit to work -Removed the defected UV relay -Installed the new relay and tighten all wires -Adjusted the setting of over/under voltage -De-isolate for test. -Verify operation of ATS -Trip Incomer-A and check that incomer-B closed and supply the loads -Trip Inc-B and check that Inc-A remain closed and supply the loads. -Restore Inc-A supply and check Inc-B tripped and incomer-A closed. -De-isolate & close work permit. | AMR GAMAL | 2026-06-25 | BAZYA DMIITRIY | 2026-06-25 | Complete |  | WO210000345187.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/4eace83f-b604-4583-a96b-588e80c84360/supervisor/210000345187_19HVPT_SS_20260624084418.pdf | {"active":true,"addedAt":"2026-06-24T05:43:41.811Z","addedBy":"BAZYA DMIITRIY","addedByUsername":"bazya dmiitriy","woNo":"210000345187"} | 6/25/2026, 2:24:17 PM - Bulk operation confirmation By: BAZYA DMIITRIY COMPLETED / Complete 6/25/2026, 2:21:52 PM - Supervisor update By: AMR GAMAL COMPLETED PTW: 1903 -Obtained permit to work -Removed the defected UV relay -Installed the new relay and tighten all wires -Adjusted the setting of over/under voltage -De-isolate for test. -Verify operation of ATS -Trip Incomer-A and check that incomer-B closed and supply the loads -Trip Inc-B and check that Inc-A remain closed and supply the loads. -Restore Inc-A supply and check Inc-B tripped and incomer-A closed. -De-isolate & close work permit. 6/24/2026, 3:18:41 PM - Operation returned By: BAZYA DMIITRIY ONGOING / Incomplete 6/24/2026, 11:46:06 AM - Supervisor update By: AMR GAMAL COMPLETED PTW: 1903 -Obtained permit to work -Removed the defected UV relay -Installed the new relay and tighten all wires -Adjusted the setting of over/under voltage -De-isolate for test. -Verify operation of ATS -Trip Incomer-A and check that incomer-B closed and supply the loads -Trip Inc-B and check that Inc-A remain closed and supply the loads. -Restore Inc-A supply and check Inc-B tripped and incomer-A closed. -De-isolate & close work permit. 6/24/2026, 11:44:27 AM - Attachment uploaded By: AMR GAMAL ONGOING 19HVPT SS - 210000345187.pdf 6/24/2026, 8:43:41 AM - CM's for tomorrow By: BAZYA DMIITRIY ONGOING Added to CM's for tomorrow by BAZYA DMIITRIY. Created from notification 110000400173 by HUSSAIN OTHMAN at 2026-06-24T05:33:07.667Z
W25-26 | 2026-06-19 | 110000399762 | PPG | 19DCS | CM | 210000344977 | 19DCS | CARRY OUT CM TO CHECK AND FIX WATER INLET VLV FROM DCS (OPEN AND CLOSE COMMANDS) | Z019-5000-90GAC10AA008 | PNEUGLOBE VLV RIVER/SEA/MOD PIPE LINE |  |  |  | 2026-06-23 | COMPLETED |  |  | 1 |  | 3 |  | 3 |  |  | ABDELRAZEK SAID MOHAMED; MESSAOUD BENMOUIZA; MOHAMED BOUCHACHIA | After the reset from logic, the issue was resolved | MOHAMED BOUCHACHIA | 2026-06-23 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 210000344977.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/35a41f6b-9cfb-4b54-84a1-d1f988a58c08/210000344977_19DCS_20260619114022.pdf WO_210000344977.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/bc6ea8f0-d1b3-4dd4-80b1-45fdd038eeec/supervisor/210000344977_19DCS_20260623111407.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/23/2026, 2:17:51 PM - Bulk supervisor update By: MOHAMED BOUCHACHIA COMPLETED After the reset from logic, the issue was resolved 6/23/2026, 2:14:10 PM - Attachment uploaded By: MOHAMED BOUCHACHIA ONGOING 19DCS - 210000344977 (2).pdf 6/19/2026, 6:23:20 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:40:26 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19DCS - 210000344977.pdf Created from notification 110000399762 by HUSSAIN OTHMAN at 2026-06-19T11:38:48.991Z
W25-26 | 2026-06-19 | 110000399602 | PPG | 19MSTAT | CM | 210000344970 | 19MSTAT | CARRY OUT CM TO CHECK & FIX THE EYE WASH IN CHEMICAL AREA OF WTP | Z019-7000-90GCN09AX001 | CHEMICAL AREA - EYE WASH WITH SHOWER |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1911 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED ,ONE NOZZLE IS MISSING | CHIKH SOUHEIB | 2026-06-26 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 01.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/e48981a0-81ab-460f-9afa-00d39c5d9002/supervisor/210000344970_19MSTAT_20260626114314.pdf | {"active":true,"addedAt":"2026-06-23T07:16:43.760Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000344970"} | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 2:53:42 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1911 INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED ,ONE NOZZLE IS MISSING 6/26/2026, 2:43:16 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344970.pdf 6/23/2026, 10:16:43 AM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/20/2026, 4:29:49 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344970.pdf 6/19/2026, 6:20:24 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:43:37 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344970.pdf Created from notification 110000399602 by HUSSAIN OTHMAN at 2026-06-19T11:35:11.719Z
W25-26 | 2026-06-22 | 110000399443 | PPG | 19MROT | CM | 210000344702 | 19MROT | CARRY OUT CM TO CHECK AND FIX AIR LEAKAGE FROM FLOAT DRAIN VALVE OF AIR FILTER OF CONTROL AIR COMPRESSOR NO.1 | Z019-4702-12MBX35AT010 | CONDENSATE SEPERATOR O/L CONT AIR COMPR1 |  |  |  | 2026-06-16 | COMPLETED |  |  | 3 |  | 2 |  | 6 | 1808 |  | ADHEM ELSAYED HANAFY; AMR MOHAMED; MOHAMED AHMED; MAHMOUD OMARA | Open work permit (1808) check item subject to maintenance for HSE conditions check tightness of all nuts and bolts checked and cleaned inlet air filter check and cleaned cooler check for absence of dangerous vibrations and abnormal noise Replaced water separator PD and DD with control drain valve by new . check perfect condition of all accessories installed Perform test run and compressor working with normal operation condition clean area and equipment after the work inform control room of ending of the works close the work permit | MAHMOUD OMARA | 2026-06-23 | AHMED ABDULLAH | 2026-06-28 | Complete |  | Control Compressor (1)GTG 12.pdf.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/32e8536b-ec92-4cdf-a317-bbf38e25fba1/supervisor/210000344702_19MROT_20260623070310.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/23/2026, 10:06:34 AM - Supervisor update By: MAHMOUD OMARA COMPLETED PTW: 1808 Open work permit (1808) check item subject to maintenance for HSE conditions check tightness of all nuts and bolts checked and cleaned inlet air filter check and cleaned cooler check for absence of dangerous vibrations and abnormal noise Replaced water separator PD and DD with control drain valve by new . check perfect condition of all accessories installed Perform test run and compressor working with normal operation condition clean area and equipment after the work inform control room of ending of the works close the work permit 6/23/2026, 10:03:12 AM - Attachment uploaded By: MAHMOUD OMARA ONGOING 19MROT - 210000344702.pdf
W25-26 | 2026-06-19 | 110000399657 | PPG | 19MSTAT | CM | 210000344974 | 19MSTAT | CARRY OUT CM TO CHECK AND FIX AIR LEAKAG | Z019-4702-12MBL53 | PULSE FILTER SYSTEM |  |  |  | 2026-06-22 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1676 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | AIR LEAKAGE FIXED BY COLD WELDING UNDER PTW#1676 (CARRY OUT CM TO CLEAN PULSE FILTER) | CHIKH SOUHEIB | 2026-06-22 | AHMED ABDULLAH | 2026-06-28 | Complete |  | WhatsApp Image 2026-06-22 at 18.12.02.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/29ecb2c8-55ce-4717-941e-c3a91e531666/supervisor/210000344974_19MSTAT_20260622151352.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/22/2026, 6:18:37 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1676 AIR LEAKAGE FIXED BY COLD WELDING UNDER PTW#1676 (CARRY OUT CM TO CLEAN PULSE FILTER) 6/22/2026, 6:13:54 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344974.pdf 6/20/2026, 4:30:06 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344974.pdf 6/19/2026, 6:21:40 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:41:44 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344974.pdf Created from notification 110000399657 by HUSSAIN OTHMAN at 2026-06-19T11:37:42.263Z
W25-26 | 2026-06-16 | 110000399233 | ZUBAIR MV SS | 19HVPT SS | CM | 210000344726 | 19HVPT SS | CARRY OUT CM TO FIX DAMAGED LADDER OF EARTHING PIT 01 ZM MV SS | Z912-9450-AR02-EP01 | EARTHING PIT 01 |  |  |  | 2026-06-23 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | AHMED HUSSIEN; AMER JAMAL; AMR GAMAL; HASHIM ISMAIL; ISLAM FATHI; KAREEM ABDELMAWLA; KARIM DALY; MOHAMMED KHALIF; RAMADAN GAMAL; SAAD AWNY | CM to fix MV SS Ladder has been done. | MOHAMMED KHALIF | 2026-06-24 | BAZYA DMIITRIY | 2026-06-24 | Complete |  | WO 210000344726.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/2ee38197-b7e6-4d03-b3ad-772a9f261610/supervisor/210000344726_19HVPT_SS_20260624063040.pdf | {"active":true,"addedAt":"2026-06-22T10:38:05.420Z","addedBy":"BAZYA DMIITRIY","addedByUsername":"bazya dmiitriy","woNo":"210000344726"} | 6/24/2026, 9:51:09 AM - Bulk operation confirmation By: BAZYA DMIITRIY COMPLETED / Complete 6/24/2026, 9:36:48 AM - Supervisor update By: MOHAMMED KHALIF COMPLETED CM to fix MV SS Ladder has been done. 6/24/2026, 9:30:43 AM - Attachment uploaded By: MOHAMMED KHALIF ONGOING 19HVPT SS - 210000344726.pdf 6/22/2026, 1:38:05 PM - CM's for tomorrow By: BAZYA DMIITRIY ONGOING Added to CM's for tomorrow by BAZYA DMIITRIY. 6/19/2026, 8:14:48 AM - Bulk supervisor update By: AMR GAMAL ONGOING ONGOING Created from notification 110000399233 by Abdelnasser at 2026-06-16T05:34:37.404Z
W24-26 | 2026-06-10 | 110000398846 | PPG | 19INSTR | CM | 210000344487 | 19INSTR | CARRY OUT CM TO CHECK AND FIX THE FAILEAR VALVE OPEN | Z019-4600-90QFA01AA003 | SOL VLV AIR RECEIVER O/L TO SERV AIR |  |  |  | 2026-06-20 | COMPLETED |  |  | 2 |  | 5 |  | 10 | 1853 |  | HAITHAM MOHAMED; INST-SPV; MOHAMMED HAMED; MOHAMED TOUNI; SAHAYARAJ | Dismantled the air supply, replaced by another ss tube from another source, support the new impulse tube, air leakage test done was ok no air leakage found, Valve Component Checked, ensured smooth travel without sticking ensured the feedback in HMI was ok no problem | MOHAMED TOUNI | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | WO#210000344487 20-Jun-2026 16-09-33.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/9fc5cdab-1504-4a30-82ba-3dc9813e9d62/210000344487_19INSTR_20260620131734.pdf | {"active":true,"addedAt":"2026-06-19T09:41:58.528Z","addedBy":"MOHAMED TOUNI","addedByUsername":"mtouni","woNo":"210000344487"} | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/22/2026, 10:39:32 AM - Attachment deleted By: SYSTEM ADMIN COMPLETED 19INSTR - 210000344487.pdf 6/20/2026, 4:27:02 PM - Supervisor update By: MOHAMED TOUNI COMPLETED PTW: 1853 Dismantled the air supply, replaced by another ss tube from another source, support the new impulse tube, air leakage test done was ok no air leakage found, Valve Component Checked, ensured smooth travel without sticking ensured the feedback in HMI was ok no problem 6/20/2026, 4:17:36 PM - Attachment uploaded By: MOHAMED TOUNI ONGOING 19INSTR - 210000344487 (2).pdf 6/20/2026, 1:34:08 PM - Attachment uploaded By: IMAN ONGOING 19INSTR - 210000344487.pdf 6/19/2026, 12:41:58 PM - CM's for tomorrow By: MOHAMED TOUNI ONGOING Added to CM's for tomorrow by MOHAMED TOUNI.
W25-26 | 2026-06-18 | 110000399701 | PPG | 19CCTV | CM | 210000344925 | 19CCTV | CARRY OUT CM TO REPLACE DAMAGED LCD Console "90CYD00XD001" with Integrated 8 Port Analog KVM Switch IN SECURITY BUILDING TELECOM ROOM | Z019-9600-90CYD00YX001 | WORKSTATION SERVER 1 IN SECURITY BUILDI |  |  |  | 2026-06-19 | COMPLETED |  |  | 2 |  | 1 |  | 2 | 1850 |  | AHMED LEKROUNE | DAMAGED LCD REPLACED BY WORKING ONE - TESTED AND WORKING. TASKS COMPLITED | AHMED LEKROUNE | 2026-06-19 | MOSTAFA AHMED ELSANDOBY | 2026-06-22 | Complete |  | 210000344925 - CCTV.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/a2b294fc-50ad-4a99-9f09-eabe6f792f51/210000344925_19CCTV_20260619083552.pdf | {"active":false,"addedAt":"2026-06-19T07:20:43.520Z","addedBy":"AHMED LEKROUNE","addedByUsername":"ahmed lekroune","woNo":"210000344925","removedAt":"2026-06-19T08:21:58.984Z","removedBy":"AHMED LEKROUNE","removedByUsername":"ahmed lekroune"} | 6/22/2026, 11:27:41 PM - Bulk operation confirmation By: MOSTAFA AHMED ELSANDOBY COMPLETED / Complete 6/19/2026, 11:37:07 AM - Supervisor update By: AHMED LEKROUNE COMPLETED PTW: 1850 DAMAGED LCD REPLACED BY WORKING ONE - TESTED AND WORKING. TASKS COMPLITED 6/19/2026, 11:35:56 AM - Attachment uploaded By: AHMED LEKROUNE ONGOING 19CCTV - 210000344925.pdf 6/19/2026, 11:34:37 AM - Attachment deleted By: AHMED LEKROUNE ONGOING 19CCTV - 210000344925.pdf 6/19/2026, 11:27:26 AM - Attachment uploaded By: AHMED LEKROUNE ONGOING 19CCTV - 210000344925.pdf 6/19/2026, 10:20:43 AM - CM's for tomorrow By: AHMED LEKROUNE ONGOING Added to CM's for tomorrow by AHMED LEKROUNE. 6/18/2026, 8:56:32 AM - Work order details edit By: IMAN ONGOING Details edited by IMAN Created from notification 110000399701 by IMAN at 2026-06-18T05:55:20.664Z
W25-26 | 2026-06-19 | 110000399660 | PPG | 19MSTAT | CM | 210000344976 | 19MSTAT | CARRY OUT CM TO REPLACE LUBE OIL FILTER-1 OF GT11 | Z019-4701-11MBV21AT001 | FILT LO CENTRIFUGAL PUMP1 SUCT OF LO MOD |  |  |  | 2026-06-19 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1755 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | FILTERS REPLACED | CHIKH SOUHEIB | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | LUBE OIL.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/94a3b962-62a8-4129-8657-5248f88fc0ca/210000344976_19MSTAT_20260620145638.pdf |  | 6/28/2026, 3:38:14 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/20/2026, 6:06:38 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1755 FILTERS REPLACED 6/20/2026, 5:56:39 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344976.pdf 6/20/2026, 4:53:38 PM - System Admin returned confirmed WO By: SYSTEM ADMIN ONGOING / Returned to ONGOING Confirmation cleared by SYSTEM ADMIN 6/20/2026, 4:47:08 PM - Attachment deleted By: SYSTEM ADMIN ONGOING 19MSTAT - 210000344976.pdf 6/20/2026, 3:28:03 PM - Attachment uploaded By: SYSTEM ADMIN ONGOING 19MSTAT - 210000344976.pdf 6/20/2026, 3:27:08 PM - Attachment deleted By: SYSTEM ADMIN ONGOING 19MSTAT - 210000344976.pdf 6/20/2026, 3:16:43 PM - Admin full edit By: SYSTEM ADMIN ONGOING All-column edit by SYSTEM ADMIN 6/20/2026, 3:14:47 PM - Admin full edit By: SYSTEM ADMIN ONGOING All-column edit by SYSTEM ADMIN 6/20/2026, 10:26:57 AM - Bulk operation confirmation By: SABER MOHAMED COMPLETED / Complete Work Completed 6/20/2026, 7:48:04 AM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1755 FILTERS WERE REPLACED 6/19/2026, 6:22:44 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 6:12:30 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:41:00 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344976.pdf Created from notification 110000399660 by HUSSAIN OTHMAN at 2026-06-19T11:38:32.376Z
W25-26 | 2026-06-16 | 110000399273 | PPG | 19FAG | CM | 210000344727 | 19FAG | CARRY OUT CM TO REPLACE MANUAL RELEASE PUSH BUTTON FOR GT13 (13CYE10CH25Y-S52) | Z019-7000-13CYE10CH25Y-S52 | MANUAL PUSH BUTTON |  |  |  | 2026-06-14 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | The manual call point was replaced with a new unit. Verified the fire alarm control panel, and all systems are normal. | LITMAN GEORGE | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 344727.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/3b07e75a-4467-4e18-8161-8295b3a96483/210000344727_19FAG_20260620104710.pdf |  | 6/28/2026, 3:55:26 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/20/2026, 1:51:01 PM - Supervisor update By: LITMAN GEORGE COMPLETED The manual call point was replaced with a new unit. Verified the fire alarm control panel, and all systems are normal. 6/20/2026, 1:47:12 PM - Attachment uploaded By: LITMAN GEORGE ONGOING 19FAG - 210000344727.pdf Created from notification 110000399273 by Abdelnasser at 2026-06-16T05:48:06.424Z
W25-26 | 2026-06-14 | 110000399439 | PPG | 19FAG | CM | 210000344637 | 19FAG | CARRY OUT CM TO CHECK AND FIX FAULT ON GAS DETECTOR AT FUEL GAS MODULE | Z019-7000-14CYQ10CQ291 | ALARM PNL FOR IR-GAS DETC FG CONTL SKID |  |  |  | 2026-06-19 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | Performed a zero calibration on the detector and normalized it; the detector is now healthy. | LITMAN GEORGE | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 344637.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/b194e78f-7f0f-41fb-9e99-47480a7d2b7e/210000344637_19FAG_20260620104625.pdf |  | 6/28/2026, 3:55:26 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/20/2026, 1:49:24 PM - Supervisor update By: LITMAN GEORGE COMPLETED Performed a zero calibration on the detector and normalized it; the detector is now healthy. 6/20/2026, 1:46:27 PM - Attachment uploaded By: LITMAN GEORGE ONGOING 19FAG - 210000344637.pdf 6/14/2026, 9:48:12 AM - Work order details edit By: ABDELNASSER ONGOING Details edited by Abdelnasser 6/14/2026, 9:39:47 AM - Work order details edit By: ABDELNASSER ONGOING Details edited by Abdelnasser Created from notification 110000399439 by Abdelnasser at 2026-06-14T06:28:10.164Z
W25-26 | 2026-06-14 | 110000399274 | PPG | 19FAG | CM | 210000344644 | 19FAG | CARRY OUT CM TO REPLACE MANUAL RELEASE PUSH BUTTON FOR GT14 (14CYE10CH25Y-S53) | Z019-7000-14CYE10CH25Y-S53 | MANUAL PUSH BUTTON |  |  |  | 2026-06-19 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | The manual call point was replaced with a new unit. Verified the fire alarm control panel. | LITMAN GEORGE | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 344644.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/3854cd98-0e94-4bb3-b5ee-36719b448d18/210000344644_19FAG_20260620104800.pdf |  | 6/28/2026, 3:55:26 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/20/2026, 1:50:13 PM - Supervisor update By: LITMAN GEORGE COMPLETED The manual call point was replaced with a new unit. Verified the fire alarm control panel. 6/20/2026, 1:48:02 PM - Attachment uploaded By: LITMAN GEORGE ONGOING 19FAG - 210000344644.pdf 6/18/2026, 9:16:55 AM - Work order details edit By: ABDELNASSER ONGOING Details edited by Abdelnasser 6/14/2026, 9:47:36 AM - Work order details edit By: ABDELNASSER ONGOING Details edited by Abdelnasser Created from notification 110000399274 by Abdelnasser at 2026-06-14T06:43:50.565Z
W16-26 | 2026-05-30 | 110000395359 | PPG | 19GTG | CM | 210000341405 | 19GTG | CARRY OUT CM TO PERFORM LUBE OIL PURIFICATION | Z019-4702-12MBV01 | GT LUBE OIL AUXILIARIES MODULE |  |  |  | 2026-06-20 | COMPLETED |  |  | 2 |  | 1 |  | 2 | 210000341405 |  | AHMED EMARA; ALI ELSAYED | Oil purification has been performed for GT-12 | ALI ELSAYED | 2026-06-20 | AHMED ABDULLAH | 2026-06-28 | Complete |  | oil purification.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/2570e8d9-34f2-4892-8a08-efd40a329e7e/210000341405_19GTG_20260620152718.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/22/2026, 10:39:20 AM - Attachment deleted By: SYSTEM ADMIN COMPLETED 19GTG - 210000341405.pdf 6/20/2026, 6:28:19 PM - Supervisor update By: ALI ELSAYED COMPLETED PTW: 210000341405 Oil purification has been performed for GT-12 6/20/2026, 6:27:20 PM - Attachment uploaded By: ALI ELSAYED ONGOING 19GTG - 210000341405 (2).pdf 6/20/2026, 1:55:39 PM - Attachment uploaded By: IMAN ONGOING 19GTG - 210000341405.pdf
W25-26 | 2026-06-16 | 110000399434 | PPG | 19FAG | CM | 210000344729 | 19FAG | CARRY OUT CM TO CHECK AND FIX BATTERY FAULT IN FIRE & GAS PANEL AT OUTDOR DM BUILDING PANEL | Z019-7000-90CYE07GW002 | F&G PNL DM DELUGE VLV FIRE-FIGHTING SYS |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 1 |  | 2 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | Found the terminals of the batteries in slightly loose condition, after tightening the terminals battery fault got cleared. | IFTEKHAR AHMED | 2026-06-26 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 210000344729.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/6b1ddd1f-9fbd-460e-93a3-f1d64bfd6fd3/210000344729_19FAG_20260620105616.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 6:23:45 PM - Supervisor update By: IFTEKHAR AHMED COMPLETED Found the terminals of the batteries in slightly loose condition, after tightening the terminals battery fault got cleared. 6/26/2026, 6:11:20 PM - Attachment deleted By: IFTEKHAR AHMED ONGOING 19FAG - 210000344729 (2).pdf 6/26/2026, 5:51:17 PM - Operation returned By: ABDERAHMANE ONGOING / Incomplete Review the description 6/23/2026, 6:23:25 PM - Supervisor update By: IFTEKHAR AHMED COMPLETED Inspected the fire alarm panel & confirmed that no battery faults were indicated. 6/23/2026, 6:18:11 PM - Attachment uploaded By: IFTEKHAR AHMED ONGOING 19FAG - 210000344729 (2).pdf 6/20/2026, 1:56:19 PM - Attachment uploaded By: IMAN ONGOING 19FAG - 210000344729.pdf Created from notification 110000399434 by Abdelnasser at 2026-06-16T05:53:10.706Z
W26-26 | 2026-06-23 | 110000399849 | PPG | 19FAG | CM | 210000345121 | 19FAG | CARRY OUT CM TO CHECK & FIX LINE OPEN FAULT FOR IR FLAMMABLE GAS DETECTOR | Z019-7000-90CYE01CQ021 | IR FLAMMABLE GAS DETR AIR PROD PP&SS |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 1 |  | 2 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | NEW DEVICE FIXED FOR GAS DETECTOR CQ021, MSRF-110. | IFTEKHAR AHMED | 2026-06-26 | ABDERAHMANE | 2026-06-26 | Complete |  | CQ21 AIRCOMPRESSOR.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/dc2a465e-4c11-407e-8cce-14ae6df4f897/supervisor/210000345121_19FAG_20260626131813.pdf |  | 6/26/2026, 5:51:25 PM - Operation confirmed By: ABDERAHMANE COMPLETED / Complete 6/26/2026, 4:21:26 PM - Supervisor update By: IFTEKHAR AHMED COMPLETED NEW DEVICE FIXED FOR GAS DETECTOR CQ021, MSRF-110. 6/26/2026, 4:18:16 PM - Attachment uploaded By: IFTEKHAR AHMED ONGOING 19FAG - 210000345121.pdf Created from notification 110000399849 by ABDELNASSER at 2026-06-23T04:56:45.651Z
W25-26 | 2026-06-19 | 110000399603 | PPG | 19MSTAT | CM | 210000344971 | 19MSTAT | CARRY OUT CM TO CHECK & FIX THE EYE WASH IN CHEMICAL AREA OF WTP | Z019-7000-90GCN09AX002 | CHEMICAL AREA - EYE WASH WITH SHOWER |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 2.5 |  | 5 | 1911 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED | CHIKH SOUHEIB | 2026-06-26 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 02.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/d6495520-eead-48da-86f5-be0b2d43e2b8/supervisor/210000344971_19MSTAT_20260626114417.pdf | {"active":true,"addedAt":"2026-06-23T07:16:04.356Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000344971"} | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 2:52:30 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1911 INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED 6/26/2026, 2:44:19 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344971.pdf 6/23/2026, 10:16:04 AM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/20/2026, 4:29:38 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344971.pdf 6/19/2026, 6:20:44 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:43:14 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344971.pdf Created from notification 110000399603 by HUSSAIN OTHMAN at 2026-06-19T11:35:40.183Z
W25-26 | 2026-06-19 | 110000399604 | PPG | 19MSTAT | CM | 210000344972 | 19MSTAT | CARRY OUT CM TO CHECK & FIX THE EYE WASH IN DM BUILDING INSIDE BATTRY ROOM | Z019-7000-EYEWASH-03 | DM BULDING - EYE WASH |  |  |  | 2026-06-26 | COMPLETED |  |  | 2 |  | 2.5 |  | 5 | 1911 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED | CHIKH SOUHEIB | 2026-06-26 | AHMED ABDULLAH | 2026-06-28 | Complete |  | 03.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/f0d1c4a6-04f4-4f80-ab74-af3479aa58f1/supervisor/210000344972_19MSTAT_20260626114439.pdf | {"active":true,"addedAt":"2026-06-23T07:17:35.182Z","addedBy":"CHIKH SOUHEIB","addedByUsername":"chikh","woNo":"210000344972"} | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/26/2026, 2:52:30 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED PTW: 1911 INLET PIPE FLUSHED,SPRAY NOZZLES CLEANED 6/26/2026, 2:44:41 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344972.pdf 6/23/2026, 10:17:35 AM - CM's for tomorrow By: CHIKH SOUHEIB ONGOING Added to CM's for tomorrow by CHIKH SOUHEIB. 6/20/2026, 4:29:56 PM - Attachment deleted By: CHIKH SOUHEIB ONGOING 19MSTAT - 210000344972.pdf 6/19/2026, 6:20:57 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:42:34 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344972.pdf Created from notification 110000399604 by HUSSAIN OTHMAN at 2026-06-19T11:36:07.548Z
W25-26 | 2026-06-19 | 110000399655 | PPG | 19MROT | CM | 210000344973 | 19MROT | CARRY OUT CM TO CHECK AND FIX AIR LEAKAG | Z019-4703-13MBX35AT021 | ABSORPTION DRYER O/L OF CONT AIR COMPR-2 |  |  |  | 2026-06-18 | COMPLETED |  |  | 3 |  | 2 |  | 6 | 1808 |  | ADHEM ELSAYED HANAFY; AMR MOHAMED; MOHAMED AHMED; MAHMOUD OMARA | open work permit (1808) check item subject to maintenance for HSE conditions Replaced old dryer by new one due to leakage of old dryer check tightness of all nuts and bolts checked and cleaned inlet air filter check for absence of abnormal noise. check perfect condition of all accessories installed clean area and equipment after the work inform control room of ending of the works close the work permit | MAHMOUD OMARA | 2026-06-24 | AHMED ABDULLAH | 2026-06-28 | Complete |  | GT 13 Control Compressor 2 Dryer.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/42e9c9a4-7f2a-4d15-9bc4-46d364dcfd35/supervisor/210000344973_19MROT_20260624140315.pdf |  | 6/28/2026, 3:33:49 PM - Bulk operation confirmation By: AHMED ABDULLAH COMPLETED / Complete 6/24/2026, 5:04:22 PM - Supervisor update By: MAHMOUD OMARA COMPLETED PTW: 1808 open work permit (1808) check item subject to maintenance for HSE conditions Replaced old dryer by new one due to leakage of old dryer check tightness of all nuts and bolts checked and cleaned inlet air filter check for absence of abnormal noise. check perfect condition of all accessories installed clean area and equipment after the work inform control room of ending of the works close the work permit 6/24/2026, 5:03:17 PM - Attachment uploaded By: MAHMOUD OMARA ONGOING 19MROT - 210000344973.pdf 6/24/2026, 5:00:22 PM - System Admin returned confirmed WO By: SYSTEM ADMIN ONGOING / Returned to ONGOING Confirmation cleared by SYSTEM ADMIN 6/23/2026, 9:22:23 AM - Attachment deleted By: ABDELNASSER ONGOING 19MSTAT - 210000344973.pdf 6/20/2026, 3:40:44 PM - Admin full edit By: SYSTEM ADMIN ONGOING All-column edit by SYSTEM ADMIN 6/20/2026, 3:24:41 PM - Admin full edit By: SYSTEM ADMIN ONGOING All-column edit by SYSTEM ADMIN 6/20/2026, 10:22:23 AM - Bulk operation confirmation By: SABER MOHAMED COMPLETED / Complete Work Completed 6/20/2026, 8:06:50 AM - Supervisor update By: MAHMOUD OMARA COMPLETED PTW: 1808 Open work permit (1808) check item subject to maintenance for HSE conditions Replaced old dryer by new one due to leakage of old dryer check tightness of all nuts and bolts checked and cleaned inlet air filter check for absence of abnormal noise. check perfect condition of all accessories installed clean area and equipment after the work inform control room of ending of the works close the work permit 6/19/2026, 6:22:01 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 6:21:16 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 6:13:18 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by ABDELNASSER 6/19/2026, 2:42:03 PM - Attachment uploaded By: HUSSAIN OTHMAN ONGOING 19MSTAT - 210000344973.pdf Created from notification 110000399655 by HUSSAIN OTHMAN at 2026-06-19T11:36:50.179Z
W25-26 | 2026-06-18 | 110000399761 | PPG | 19MSTAT | CM | 210000344919 | 19MSTAT | CARRY OUT CM TO REPLACE PWR OIL FILTER 1 FOR GT13 DUE TO HIGH DP ALARM | Z019-4703-13MBX21AT001 | FILT-1 FOR POWER OIL IN FG CONT SKID |  |  |  | 2026-06-17 | COMPLETED |  |  | 2 |  | 2 |  | 4 | 1826 |  | ALI ELSAYED; CHIKH SOUHEIB; MSTAT-SPV; RAZIK RAHAB | filter was replaced | CHIKH SOUHEIB |  | SABER MOHAMED | 2026-06-18 | Complete | Work Completed |  | [{"name":"19MSTAT - 210000344919.pdf","originalName":"WhatsApp Image 2026-06-19 at 15.32.36.pdf","path":"4588a460-e88b-40d6-bac3-dadd0de441b5/210000344919_19MSTAT_20260619123641.pdf","url":"https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/4588a460-e88b-40d6-bac3-dadd0de441b5/210000344919_19MSTAT_20260619123641.pdf","type":"application/pdf","size":70230,"uploadedBy":"CHIKH SOUHEIB","uploadedAt":"2026-06-19T12:36:42.907Z"}]
W25-26 | 2026-06-20 | 110000400029 | PPG | 19ELEC | CM | 210000345053 | 19ELEC | LIGHTING ON CONTAINER - 20 OF AIR COMPRESSOR 90QFA20AW001 | Z019-4600-90QFA20AW001 | CONTAINER - 2 |  |  |  | 2026-06-21 | COMPLETED |  |  | 2 |  | 0.5 |  | 1 |  |  | MANISHKUMAR RATILAL PATEL; VITALIY GORSHKOV | Six lamps, each 120 cm in size, were replaced. working properly. | MANISHKUMAR RATILAL PATEL |  | ABDERAHMANE | 2026-06-21 | Complete |  |  | [{"name":"19ELEC - 210000345053.pdf","originalName":"210000345053.pdf","path":"323f5dd2-1656-4924-bee5-15ee9ee76d6b/210000345053_19ELEC_20260621074706.pdf","url":"https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/323f5dd2-1656-4924-bee5-15ee9ee76d6b/210000345053_19ELEC_20260621074706.pdf","type":"application/pdf","size":574913,"uploadedBy":"MANISHKUMAR RATILAL PATEL","uploadedAt":"2026-06-21T07:47:08.086Z"}]
W25-26 | 2026-06-14 | 110000399423 | PPG | 19ELEC | CM | 210000344634 | 19ELEC | CARRY OUT CM TO PREFORM TYPE A - INSPECTION FOR GT-12 GENERATOR | Z019-4702-12MKA10 | GAS TURBINE GENERATOR |  |  |  | 2026-06-18 | COMPLETED |  |  | 4 |  | 9 |  | 36 |  |  | MANISHKUMAR RATILAL PATEL; VITALIY GORSHKOV | GT-12 generator inspection was carried out successfully. RC shaft grounding, drive end grounding, carbon brushes, and brush holders were checked, cleaned, and verified. All components were found to be in good condition and operating normally. | MANISHKUMAR RATILAL PATEL |  | ABDERAHMANE | 2026-06-14 | Complete
W25-26 | 2026-06-16 | 110000399433 | PPG | 19FAG | CM | 210000344728 | 19FAG | CARRY OUT CM TO CHECK AND FIX THE LINE OPEN FAULT FOR LINEAR HEAT DETECTOR AT SECUIRTITY BUILDING TRANSFORMER AREA | Z019-7000-90CYE07CT031 | LHD SECU BLDG AUX TRANF AREA IN PP & SS |  |  |  | 2026-06-17 | COMPLETED |  |  | 2 |  | 3 |  | 6 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | Performed a loop check and identified a loose connection on the Linear Heat Detector (LHD) alarm resistor. Properly tightened the connection, restoring the LHD to normal operation. | LITMAN GEORGE |  | ABDERAHMANE | 2026-06-17 | Complete
W25-26 | 2026-06-16 | 110000399437 | PPG | 19FAG | CM | 210000344731 | 19FAG | CARRY OUT CM TO CHECK AND FIX LINE OPEN FAUT FOR LINEAR HEAT DETECTOR AT DM BUILDING AUX TRANSFORMER AREA | Z019-7000-90CYE07CT024 | LHD DM BLDG AUX TRANF AREA IN PP & SS |  |  |  | 2026-06-18 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | IFTEKHAR AHMED; LITMAN GEORGE; BHUPENDRASINH PRAVINSINH VALA; VIVEKBHAI NATVARBHAI PATEL | Performed a loop check and identified a loose connection on the Linear Heat Detector (LHD) alarm resistor. Properly tightened the connection, restoring the LHD to normal operation. | LITMAN GEORGE |  | ABDERAHMANE | 2026-06-17 | Complete
W20-26 | 2026-05-15 | 110000397465 | NEW RAFIDIYA MV SS | 19HVPT SS | CM | 210000342803 | 19HVPT SS | CARRY OUT CM TO CHECK & FIX TIGHTING CT | Z971-9100-EH-401-K07 | 11KV OUTGOING FEEDER-6, FOR R-IPF | 2026-05-15 |  | 2026-05-20 | 2026-05-26 | COMPLETED |  |  | 2 |  | 6 |  | 12 |  |  | AHMED HUSSIEN; AMER JAMAL; AMR GAMAL; HASHIM ISMAIL; islam fathi; Kareem Abdelmawla; MOHAMMED KHALIF; ramadan gamal; SAAD AWNY | CT of the feeder tested with normal result. The technical report submitted | ALEXY | 2026-05-26 | ALEXY | 2026-05-26 | Complete | Work completed, equipment returned in service |  |  | 5/26/2026, 10:27:13 AM - Bulk operation confirmation By: ALEXY COMPLETED / Complete Work completed, equipment returned in service 5/26/2026, 10:21:00 AM - Supervisor update By: ALEXY COMPLETED CT of the feeder tested with normal result. The technical report submitted
W20-26 | 2026-05-10 | 110000397101 | LSC HV SS | 19FAG SS | CM | 210000342641 | 19FAG SS | CARRY OUT CM FOR CHECK & REPAIR EXTINGUISHANT CONTROL PANEL FAULT | Z930-7000-JY-004 | IN MOD FOR EXT PANEL MONITOR FOR LSC S/S | 2026-05-10 |  | 2026-05-16 | 2026-05-26 | COMPLETED |  |  | 2 |  | 6 |  | 12 |  |  | EMAD MUSTAFA; SPV-SS | The system cleared and tested after returned back in service | ALEXY | 2026-05-26 | ALEXY | 2026-05-26 | Complete | Work completed, equipment returned in service |  |  | 5/26/2026, 10:27:13 AM - Bulk operation confirmation By: ALEXY COMPLETED / Complete Work completed, equipment returned in service 5/26/2026, 10:16:06 AM - Supervisor update By: ALEXY COMPLETED The system cleared and tested after returned back in service 5/26/2026, 10:16:02 AM - Supervisor update By: ALEXY COMPLETED The system cleared and tested after returned back in service
W20-26 | 2026-05-10 | 110000397105 | NEW RAFIDIYA MV SS | 19HVAC SS | CM | 210000342564 | 19HVAC SS | CARRY OUT CM FOR THE AIR CONDITIONER UNIT HAS A CONTINUOUS ALARM | Z913-6600-EG-401C | AIR COOLED CONDENSING UNITS-CONT CABIN | 2026-05-10 |  | 2026-05-16 | 2026-05-26 | COMPLETED |  |  | 4 |  | 4 |  | 16 |  |  | AHMED MAGID; Farag | The ACU fixed, tested and putted in service | ALEXY | 2026-05-26 | ALEXY | 2026-05-26 | Complete | Work completed, equipment returned in service |  |  | 5/26/2026, 10:27:13 AM - Bulk operation confirmation By: ALEXY COMPLETED / Complete Work completed, equipment returned in service 5/26/2026, 10:17:42 AM - Supervisor update By: ALEXY COMPLETED The ACU fixed, tested and putted in service
W21-26 | 2026-05-30 | 110000397617 | PPG | 19ELEC | CM | 210000342867 | 19ELEC | CARRY OUT CM TO CHECK AND FIX FAN FAILURE ALARM IN BATTERY CHARGER | Z019-4702-12BTL10 | BATTERY CHARGER FOR GAS TURBINE-2 DC UPS |  |  |  | 2026-06-13 | COMPLETED |  |  | 3 |  | 2 |  | 6 |  |  | MANISHKUMAR RATILAL PATEL; VITALIY GORSHKOV | During the inspection, a fan malfunction was identified. The faulty fan was replaced with a new one. After replacement, an operational check was carried out. The fan is functioning normally, and no issues were found. | VITALIY GORSHKOV | 2026-06-13 | MOSTAFA AHMED ELSANDOBY | 2026-06-14 | Complete |  | WO#210000342867.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/6ac2363f-6947-4e3c-a7c5-157cb8b4b975/210000342867_19ELEC_20260613072051.pdf | {"active":false,"addedAt":"2026-06-11T10:29:46.378Z","addedBy":"MANISHKUMAR RATILAL PATEL","addedByUsername":"manish","woNo":"210000342867","removedAt":"2026-06-12T10:09:41.098Z","removedBy":"MANISHKUMAR RATILAL PATEL","removedByUsername":"manish"} | 6/14/2026, 3:32:23 PM - Operation confirmed By: MOSTAFA AHMED ELSANDOBY COMPLETED / Complete 6/13/2026, 10:21:21 AM - Bulk supervisor update By: VITALIY GORSHKOV COMPLETED During the inspection, a fan malfunction was identified. The faulty fan was replaced with a new one. After replacement, an operational check was carried out. The fan is functioning normally, and no issues were found. 6/13/2026, 10:20:53 AM - Attachment uploaded By: VITALIY GORSHKOV ONGOING WO#210000342867.pdf 6/11/2026, 1:29:46 PM - CM's for tomorrow By: MANISHKUMAR RATILAL PATEL ONGOING Added to CM's for tomorrow by MANISHKUMAR RATILAL PATEL. 6/11/2026, 1:29:04 PM - Supervisor update By: MANISHKUMAR RATILAL PATEL ONGOING waiting for GTG 12 shutdown(island mode) 6/1/2026, 9:53:51 AM - Supervisor update By: MANISHKUMAR RATILAL PATEL ON HOLD / SD-GT12 waiting for GTG 12 shutdown(island mode)
W24-26 | 2026-06-10 | 110000398757 | PPG | 19MSTAT | CM | 210000344486 | 19MSTAT | CHECK & FIX THE FUEL GAS SCRUBBER 1 RECEVIED HIGH LEVEL ALARAM ON UPPER SECTION OF FUEL GAS SCRUBBER 1 & AUTOMATIC DRAIN NOT WORKING | Z019-4200-90EKB01CL002 | LEVEL TRANS FOR FUEL GAS SCRUBBER 1 |  |  |  | 2026-06-14 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | ALI ELSAYED ABD ELHAMID; chikh souheib; MSTAT-SPV; RAZIK RAHAB | automatic drain removed to workship for internal parts inspection and testing | CHIKH SOUHEIB | 2026-06-14 | ABDERAHMANE | 2026-06-14 | Complete |  | sautomatic drain .pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/2662121a-49d2-42a4-a1b0-b15e625d7fa2/210000344486_19MSTAT_20260614082008.pdf |  | 6/14/2026, 2:23:48 PM - Operation confirmed By: ABDERAHMANE COMPLETED / Complete 6/14/2026, 11:22:37 AM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED automatic drain removed to workship for internal parts inspection and testing 6/14/2026, 11:20:11 AM - Attachment uploaded By: CHIKH SOUHEIB ONGOING sautomatic drain .pdf 6/10/2026, 2:43:40 PM - Work order details edit By: ABDELNASSER ONGOING Details edited by Abdelnasser
W24-26 | 2026-06-14 | 110000399426 | PPG | 19MSTAT | CM | 210000344639 | 19MSTAT | CARRY OUT CM TO REPLACE OIL LUBE FILTER 2 OF GT14 DUE TO HIGH DP | Z019-4704-14MBV21AT002 | FILT LO CENTRIFUGAL PUMP2 SUCT OF LO MOD |  |  |  | 2026-06-13 | COMPLETED |  |  | 2 |  | 2 |  | 4 |  |  | ALI ELSAYED ABD ELHAMID; chikh souheib; MSTAT-SPV; RAZIK RAHAB | FILTERS WERE REPLACED | CHIKH SOUHEIB | 2026-06-14 | SABER MOHAMED | 2026-06-15 | Complete | Work Completed | LUBE OIL FILTER.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/3823ead2-cb89-4fde-8557-af1734d33e02/210000344639_19MSTAT_20260614124355.pdf |  | 6/15/2026, 8:22:26 AM - Bulk operation confirmation By: SABER MOHAMED COMPLETED / Complete Work Completed 6/14/2026, 3:50:05 PM - Bulk supervisor update By: CHIKH SOUHEIB COMPLETED FILTERS WERE REPLACED 6/14/2026, 3:43:57 PM - Attachment uploaded By: CHIKH SOUHEIB ONGOING LUBE OIL FILTER.pdf
W02-26 | 2026-01-04 | 110000387780 | PPG | 19ELEC | CM | 210000335115 | 19ELEC.P | CARRY OUT CM TO APPLY MOC OF MISMATCH RELAY SETTING WITH COORDNATION STUDY | Z019-9100-12BBT20GT200 | MV BB INCOMER CIRCUIT BREAKER | 2026-01-04 |  | 2026-01-09 | 2026-06-11 | COMPLETED |  |  | 1 |  | 8 |  | 8 |  |  | abdo ghoname; MANISHKUMAR RATILAL PATEL; VITALIY GORSHKOV | • Check relays earthing. • Check relays date and time. • Change the relay setting to be like coordination study • Test the activating of protection functions by secondary injection (Overcurrent, Short Circuit and Earth Fault). • Check relays earthing. • Check relays date and time. | ABDO GHONAME | 2026-06-12 | MOSTAFA AHMED ELSANDOBY | 2026-06-14 | Complete |  | WO scan .pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/6ea87e33-18d3-4d8e-9173-cca3a00c805f/210000335115_19ELEC_P_20260612122402.pdf |  | 6/14/2026, 3:37:12 PM - Bulk operation confirmation By: MOSTAFA AHMED ELSANDOBY COMPLETED / Complete 6/12/2026, 3:28:52 PM - Supervisor update By: ABDO GHONAME COMPLETED • Check relays earthing. • Check relays date and time. • Change the relay setting to be like coordination study • Test the activating of protection functions by secondary injection (Overcurrent, Short Circuit and Earth Fault). • Check relays earthing. • Check relays date and time. 6/12/2026, 3:24:05 PM - Attachment uploaded By: ABDO GHONAME ON HOLD / SD-GT12 WO scan .pdf
W18-26 | 2026-05-01 | 110000396445 | PPG | 19INSTR | CM | 210000342144 | 19INSTR | CARRY OUT CM TO CHECK AND FIX THE DISTURBANCE ALARM OF RELIEF VALVE | Z019-4702-12MBP06AA241 | SHUT-BALL VALVE FG IN FG SUPPLY BLOCK | 2026-05-01 |  | 2026-05-07 | 2026-06-10 | COMPLETED |  |  | 2 |  | 6 |  | 12 |  |  | HAITHAM MOHAMED; INST-SPV; MOHAMMED HAMED; MOHAMED TOUNI; SAHAYARAJ | After the power supply reset for the MOV, Alarm was disappeared. And all terminal tightness checked, cleaned contact points in the electrical contactor. now MOV valve working from Local/DCS normal. stoke tested. found now normal. | SAHAYARAJ | 2026-06-16 | SABER MOHAMED | 2026-06-19 | Complete | Work Completed | 12MBP06AA241.pdf ¦ https://kyrznoubgnhztszvarqe.supabase.co/storage/v1/object/public/work-order-attachments/766c872f-1bc7-46b0-8268-9cd737e0f574/210000342144_19INSTR_20260616062207.pdf | {"active":false,"addedAt":"2026-06-10T08:21:55.102Z","addedBy":"Sahayaraj","addedByUsername":"sahayaraj","woNo":"210000342144","removedAt":"2026-06-13T08:25:19.376Z","removedBy":"Sahayaraj","removedByUsername":"sahayaraj"} | 6/19/2026, 2:42:31 PM - Bulk operation confirmation By: SABER MOHAMED COMPLETED / Complete Work Completed 6/16/2026, 9:26:50 AM - Supervisor update By: SAHAYARAJ COMPLETED After the power supply reset for the MOV, Alarm was disappeared. And all terminal tightness checked, cleaned contact points in the electrical contactor. now MOV valve working from Local/DCS normal. stoke tested. found now normal. 6/16/2026, 9:22:11 AM - Attachment uploaded By: SAHAYARAJ ONGOING 12MBP06AA241.pdf 6/10/2026, 11:21:55 AM - CM's for tomorrow By: SAHAYARAJ ONGOING Added to CM's for tomorrow by Sahayaraj. 6/10/2026, 11:21:35 AM - Supervisor update By: SAHAYARAJ ONGOING BY SPV FEEDBACK
W12-26 | 16-Mar-26 | 110000393391 | PPG | 19ELEC | CM | 210000339914 | 19ELEC | CARRY OUT CM TO CHECK AND FIX THE DOOR FOR GCB CONTROL PANEL FOR GT #11 | Z019-9100-11BAC20 | CIRCUIT BREAKER FOR GENERATOR-1 | 16-Mar-2026 |  | 22-Mar-2026 | 22-Apr-2026 | COMPLETED |  | 2 | 2 | 3 | 3 | 6 | 6 |  |  |  | DONE -E
W12-26 | 17-Mar-26 | 110000393388 | NEW ZUBAIR MV SS | 19HVPT SS | CM | 210000339907 | 19HVPT SS | CARRY OUT CM TO CHECK & FIX TRIP CB QB1 | Z913-9200-EL-102 | LIGHTING & SMALL POWER DB (LSPDB) | 17-Mar-2026 |  | 23-Mar-2026 | 13-May-2026 | COMPLETED |  | 3 | 3 | 3 | 3 | 9 | 9 |  |  |  | WORK DONE
W08-26 | 15-Feb-26 | 110000391402 | PPG | 19FAG | CM | 210000337993 | 19FAG | CARRY OUT CM TO CHECK AND FIX FIRE AND GAS PANEL IS HANGING TOO MANY TIMES IN TECHNICAL ROOM IN CCB | Z019-7000-90CYE01GW003 | CENTRAL FIRE & GAS PNL CCB (UCB) PP & SS | 15-Feb-2026 |  |  |  | CANCELED | [10 empty] | COVERED BY 210000338642
W39-25 | 12-Feb-26 | 110000391205 | PPG HV SS | 19HVPT SS | CM | 210000337823 | 19HVPT SS | CARRY OUT CM TO CHECK AND FIX THE METER DEVICE (P409-E17) PROBLEM IN PPG SS - REFRENCE TO WO # 2120253943418 | Z999-9700-90ARA15 | CONTROL & PROTECT PANEL FOR TR05 PPG S/S |  |  |  | 5-Mar-2026 | COMPLETED |  | 2 | 2 | 2 | 2 | 4 | 4 |  |  |  | THE METER REBLACED BY NEW ONE , NOW IN SERVICE
W13-23 | 09-Feb-26 | 110000391110 | PPG | 19MSTAT | CM | 210000337752 | 19MSTAT | CARRY OUT CM TO CHECK AND FIX PIPE BROKEN FOR AIR RELEASE VALVE REFERENCE TO WO#2120231335394 | Z019-5220-90GCF22AA216 | AIR RELEASE VALVE FOR SWRO SYSTEM |  |  |  |  | COMPLETED |  | 2 | 2 | 2 | 2 | 4 | 4 |  |  |  | DONE
W12-23 | 09-Feb-26 | 110000391104 | PPG | 19MSTAT | CM | 210000337751 | 19MSTAT | CARRY OUT CM TO CHECK AND REPLACE MALFUNCTIONED SAMPLE VALVES OF SWRO CONTAINER 2 / SWRO UNIT 2/2 FOR 1ST STAGE RO SYSTEM , THEY ARE BROKEN REFERENCE TO WO#2120231234393 | Z019-5220-90GCF22AK001 | SWRO CONTR2/ SWRO UNIT2/21ST STG RO SYS |  |  |  |  | COMPLETED |  | 2 | 2 | 2 | 2 | 4 | 4 |  |  |  | DONE
W49-25 | 30-Nov-25 | 110000384783 | PPG | 19FAG | CM | 210000332378 | 19FAG | CARRY OUT CM TO CHECK AND FIX MANUAL RELEASE PUSH BUTTON (90BFT50, 90BFT60) NOT WORKING | Z019-7000-90CYE01GK001 | FIRE ALARM HW MIMIC PANEL AT CCB (UCB) | 30-Nov-2025 |  | 7-Dec-2025 |  | CANCELED | [10 empty] | COVERED BY 210000338642
W05-26 | 28-Jan-26 | 110000389903 | PPG | 19ELEC | CM | 210000336928 | 19ELEC | CARRY OUT CM TO CHECK AND FIX RECOVERY PIT#1 PUMP#1 NOT WORKING | Z019-5900-90GMA04AP001 | TXFR PUMP 1 OIL & FIRE RECOVERY PIT 1 | 28-Jan-2026 |  | 4-Feb-2026 |  | CANCELED | [10 empty] | COVERED BY 210000342868
W32-25 | 03-Aug-25 | 110000374931 | PPG | 19MSTAT | CM | 210000322812 | 19MSTAT | CARRY OUT CM TO CHECK AND FIX THE AIR DRYER- 1 FOR COMPRESSOR AIRSTATION, REFER TO WO (2120253134775) | Z019-4701-11MBL54AT011 | AIR DRYER-1 FOR COMPRESSOR AIR STATION | 3-Aug-2025 |  | 10-Aug-2025 | 19-Oct-2025 | COMPLETED |  | 2 | 2 | 2 | 2 | 4 | 4 |  |  |  | DONE